## upload201222
Model Name |  | York | YMFE24BNJMCMO-X | YMFE36BNJMCMO-X | YMFE48BNJMCMS-X | YMFE60BNJMCMS-X
Power supply |  | V-Ph-Hz | 208/230V-1Ph-60Hz | 208/230V-1Ph-60Hz | 208/230V-1Ph-60Hz | 208/230V-1Ph-60Hz
Cooling | Rated Capacity | Btu/h | 22800 | 34200 | 46500 | 57000
| Range Capacity | Btu/h | 22800-25200 | 34200-37800 | 46500-49400 | 57000-62500
| Rated EER | Btu/h.W | 11 | 11 | 11.5 | 11.5
Heating | SEER |  | 14 | 14 | 14 | 14
Minimum Circuit Amperes |  | A | 13.7 | 21.4 | 26.9 | 32.9
Maximum Over Protecter |  | A | 20 | 30 | 40 | 50
Compressor | Model |  | PA200M2CS-3MUU1 | ASG300N1UMT | ABG042KAA | ABA051KAB
| Type |  | Rotary | Rotary | Scroll | Scroll
| Capacity | Btu/h | 20131 | 30430 | 42000 | 51500
| Input | W | 1955 | 8910 | 3962 | 4905
| Rated current(RLA) | A | 8.55 | 13.7 | 17.3 | 21.5
| Locked rotor Amp(LRA) | A | 34.8 | 72 | 108.0 | 125
| Thermal protector |  | internal | internal | internal | internal
| Capacitor | uF | 50 | 60 | 70 | 75
| Refrigerant oil | / | 750ml | 560ml | 1280±21cc | 1300cc
Indoor fan motor | Model |  | YDK150-6Z | WZDK370-312G-2 | YDK400-6Z | WZDK560-312G-1
| Type |  | AC | DC | AC | DC
| Insulation class |  | B | B | B | B
| Safe class |  | IP20 | IP20 | IP20 | IP20
| Input | W | 438 | 233 | 760 | 690
| Output | W | 150 | 375 | 400 | 560
| Rated current | A | 1.95 | 2.6 | 3.6 | 6
| Capacitor | uF | 10 | / | 20 | /
| Speed(hi/mi/lo) | r/min | 760/655/525 | 830/802/704 | 970/890/820 | 846/915/968
| Max.input | W／ＨＰ | 1/4 | 1/2 | 3/4 | 3/4
| RPM | r/min | 1075 | 1075 | 1075 | 1075
Indoor fan | material |  | Metal | Metal | Metal | Metal
| Type |  | Centrifuagal fan | Centrifuagal fan | Centrifugal fan | Centrifugal fan
| Diameter | ｉｎｃｈ | 10.28 | 10.28 | 10.98 | 10.98
| Height | ｉｎｃｈ | 9.21 | 9.21 | 10.67 | 10.67
Indoor coil | a.Number of rows |  | 4 | 4 | 4 | 3
| b.Tube pitch(a)x row pitch(b) | mm | 21 | 21*13.37 | 21*13.37 | 21*13.37
| c.Fin spacing | mm | 1.5 | 1.5 | 1.5 | 1.5
| d.Fin type (code) |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| e.Tube outside dia.and type | mm | 7 | 7 | 7 | 7
|  |  | Internal Thread | Internal Thread | Internal Thread | Internal Thread
| f.Coil length x height | mm | 670*504 | 670*504 | 837*714 | 837*714
| g.Number of circuits |  | 6 | 6 | 12 | 17
| h.Face.area／Effective heat-exchange area | ft*ft | 3.63 ft2 | 3.63 ft2 | 6.43 ft2 | 6.43 ft2
Indoor limit value of static pressure and air flow |  | Pa/m3/h | 45/1445 | 58/2074 | 70/2720 | 70/3400
Indoor sound level (sound pressure level) |  | dB(A) | 58.3 | 60.9 | 63.8 | 64.9
Outdoor fan motor | Model |  | YKS-85-6-4 | YDK110-8G-1 | YDK230-6G-1 | YDK230-6G-1
| Type |  | AC | AC | AC | AC
| Insulation class |  | B | B | B | B
| Safe class |  | IP20 | IPX4 | IP44 | IP44
| Input | W | 150 | 192 | 360 | 360
| Output | W | 85 | 110 | 230 | 230
| Rated current | A | 0.68 | 0.85 | 1.62 | 1.62
| Capacitor | uF | 6 | 6 | 15 | 15
| RPM | r/min | 1075 | 825 | 1075 | 1075
Outdoor fan | material |  | Metal | Metal | Metal | Metal
| Type |  | Axial fan | Axial fan | Axial fan | Axial fan
| Diameter | ｉｎｃｈ | 22.05 | 22 | 23-5/8 | 23-5/8
| Height | ｉｎｃｈ | 3.35 | 4.92 | 4.53 | 4.53
| Tube pitch(a)x row pitch(b) | mm | 14.5mm | 14.5mm | 14.5mm | 14.5mm
| Fin spacing | mm | 1.2mm | 1.2mm | 1.2mm | 1.2mm
| Fin type (code) |  | Hydrophilic | Hydrophilic | Hydrophilic | Hydrophilic
| Tube outside dia.and type | mm | 5mm | 5mm | 5mm | 5mm
|  |  | Internal Thread | Internal Thread | Internal Thread | Internal Thread
| Coil length x height | mm | 1713mm*522mm | 1713mm*522mm | 1928mm*754mm | 1928mm*754mm
| Number of rows |  | 2.5 | 2.5 | 2 | 2
| Number of circuits |  | 16 | 16 | 13 | 13
| h.Face area | ft*ft | 9.44 | 9.44 | 15.54 | 15.54
Outdoor air flow |  | CFM | 1960 | 2565 | 3960 | 3960
Outndoor sound level(sound pressure level ) |  | dB(A) | 58.3 | 60.9 | 63.8 | 64.9
Charged refrigerant type |  | g or kg | 2000 | 2100 | 2800 | 2900
Throttle type |  |  | Orifice | Orifice | Orifice | Orifice
Throttle size |  |  | C056 | C066 | C084 | C084
Design pressure |  | MPa | 3.79/1.72 | 3.79/1.72 | 3.79/1.72 | 3.79/1.72
Connection wiring | Power wiring | mm2 | 3*2.1（14AWG） | 3*3.3（12AWG） | 3*5.3(10AWG) | 3*8.4(8AWG)
| Signal wiring | mm2 | 5*0.8（18AWG） | 5*0.8（18AWG） | 5*0.8 (18AWG) | 5*0.8 (18AWG)
Drainage pipe outside diameter |  | mm2 | RC3/4＂ | RC3/4＂ | RC3/4＂ | RC3/4＂
Controller |  |  | Wired Controller | Wired Controller | Wired Controller | Wired Controller
Operation temp |  | ℃ | 17~30 | 17~30 | 17~30 | 17~30
Ambient temp |  | ℃ | 10~48 | 10~48 | 10~48 | 10~48
Unit | Dimension(W*H*D) | mm | 630*958*1307 | 630*958*1307 | 840*1068*1486 | 840*1068*1486
| Packing (W*H*D) | mm | 657*980*1330 | 657*980*1330 | 865*1075*1505 | 865*1075*1505
| Gross weight | Kg | 153 | 156 | 212 | 216
| Net weight | Kg | 150 | 153 | 208 | 212
Shipping Qty'Per 20GP/40GP/40'HQ |  |  | 24/50/50 | 24/50/50 | 14/30/30 | 14/30/30